## Summary
Minimizing Costs
Capital Costs
Annual Pipe costs | 81151.5611 | $/year
Annual Tank costs | 72700 | $/year
Annual Pump costs | 4554 | $/year
Diesel Generator costs | 50540 | $/year
Valve cost | 0 | $/year
Total Annual capital costs | 208945.5611 | $/year
Operational cost
Annual Pumping cost | 255851.13 | $/year
TOTAL Annual costs | 464796.6911 | $/year
Minimizing GHG emissions
Capital GHG
Annual Pipe GHG | 80077.3198 | kgCO2-e/year
Operational GHG
Annual Pumping GHG | 2833287.3 | kgCO2-e/year
TOTAL Annual GHG | 2913364.6198 | kgCO2-e/year
Minimizing Water Age
WAnet value | 0

## PipeDesign
Pipe ID | Pipe Diameter | Pipe Length | Pipe Cost/m | Pipe Cost | GHG/m | GHG
| mm | m | $/m/year | $/year | kgCO2-e/m/year | kgCO2-e/year
parallel
add3 | 356 | 107.88 | 19.94 | 2151.1272 | 28.09 | 3030.3492
add10 | 102 | 375.62 | 9.97 | 3744.9314 | 5.9 | 2216.158
add29 | 305 | 65.8 | 18.28 | 1202.824 | 23.16 | 1523.928
add30 | 254 | 68.63 | 15.55 | 1067.1965 | 18.43 | 1264.8509
add68 | 102 | 130.79 | 9.97 | 1303.9763 | 5.9 | 771.661
add101 | 406 | 567.3 | 23.26 | 13195.398 | 33.09 | 18771.957
add189 | 254 | 385.56 | 15.55 | 5995.458 | 18.43 | 7105.8708
add242 | 305 | 149.04 | 18.28 | 2724.4512 | 23.16 | 3451.7664
add270 | 305 | 70.36 | 18.28 | 1286.1808 | 23.16 | 1629.5376
add297 | 152 | 127.08 | 12.1 | 1537.668 | 9.71 | 1233.9468
add318 | 254 | 50.52 | 15.55 | 785.586 | 18.43 | 931.0836
add340 | 254 | 295.68 | 15.55 | 4597.824 | 18.43 | 5449.3824
add425 | 356 | 228.99 | 19.94 | 4566.0606 | 28.09 | 6432.3291
network expansion
1 | 102 | 328.74 | 8.31 | 2731.8294 | 5.9 | 1939.566
2 | 102 | 328.98 | 8.31 | 2733.8238 | 5.9 | 1940.982
3 | 102 | 113.05 | 8.31 | 939.4455 | 5.9 | 666.995
4 | 102 | 310.4 | 8.31 | 2579.424 | 5.9 | 1831.36
5 | 102 | 231.1 | 8.31 | 1920.441 | 5.9 | 1363.49
6 | 102 | 218.93 | 8.31 | 1819.3083 | 5.9 | 1291.687
7 | 102 | 259.37 | 8.31 | 2155.3647 | 5.9 | 1530.283
8 | 102 | 470.52 | 8.31 | 3910.0212 | 5.9 | 2776.068
9 | 102 | 244.52 | 8.31 | 2031.9612 | 5.9 | 1442.668
10 | 102 | 393.42 | 8.31 | 3269.3202 | 5.9 | 2321.178
11 | 102 | 314.33 | 8.31 | 2612.0823 | 5.9 | 1854.547
12 | 102 | 240.65 | 8.31 | 1999.8015 | 5.9 | 1419.835
13 | 102 | 293.73 | 8.31 | 2440.8963 | 5.9 | 1733.007
14 | 102 | 221.76 | 8.31 | 1842.8256 | 5.9 | 1308.384
replacements
P927 | 102 | 348.88 | 8.31 | 2899.1928 | 5.9 | 2058.392
P295 | 102 | 133.23 | 8.31 | 1107.1413 | 5.9 | 786.057
TOTAL |  |  |  | 81151.5611 |  | 80077.3198
Note: This sheet refers to both new pipes and parallel pipes. Add additional rows into the table as required (as for all other sheets).

## TankDesign
Tank ID | Added Volume | Tank Cost
| m3 | $
T4 | 500 | 14020
T5 | 500 | 14020
T6 | 500 | 14020
T7 | 1000 | 30640
TOTAL |  | 72700

## PumpDesign
Pump ID | Pump Curve | Pump Cost
$
PU12 | 8b | 4554
TOTAL |  | 4554

## ValveDesign
Valve ID | Valve Cost
$
N15 | 0
TOTAL | 0
Note: insert 0 (zero) if the valve N15 is not inserted

## DieselGenerator
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 200 | PU1 | 45.24 | 11630 | ok
|  | PU2 | 45.24
|  | PU3 | 45.24
|  | PU12 | 54.28
2 | 50 | PU4 | 31.67 | 9450 | ok
3 | 100 | PU6 | 49.76 | 10560 | ok
|  | PU7 | 49.76
4 | 50 | PU8 | 31.67 | 9450 | ok
5 | 50 | PU10 | 22.62 | 9450 | ok
|  | PU11 | 22.62
TOTAL |  |  |  | 50540